# Battery Energy Storage System (BESS)

# Emergency Response Plan

| Facility Name: | [INSERT FACILITY NAME] |
| --- | --- |
| Facility Address: | [INSERT COMPLETE ADDRESS] |
| GPS Coordinates: | [INSERT LAT/LONG] |
| Document Version: | [VERSION NUMBER] |
| Date of Issue: | [INSERT DATE] |
| Prepared By: | [INSERT NAME/ORGANIZATION] |

# TABLE OF CONTENTS

[Automatic table of contents - to be generated in final document]

1. Introduction and Scope

2. Facility Overview

3. Emergency Contact Information

4. BESS-Specific Hazards

5. Emergency Response Procedures

6. Evacuation and Assembly Points

7. Equipment and PPE Requirements

8. Training and Drills

9. Post-Incident Review Process

10. Document Control and Updates

# 1. INTRODUCTION AND SCOPE

## 1.1 Purpose

This Emergency Response Plan (ERP) provides guidance for preparing for and safely responding to emergencies at this Battery Energy Storage System (BESS) facility. This plan addresses the unique hazards associated with lithium-ion battery systems and establishes procedures that go beyond traditional electrical facility emergency planning.

## 1.2 Scope

This ERP applies to all personnel, contractors, and emergency responders involved with the operation, maintenance, or emergency response at this BESS facility. It covers:

Fire and thermal runaway incidents

Electrical hazards (arc flash, shock, stranded energy)

Toxic gas release and off-gassing events

Chemical spills or coolant leaks

Natural disasters affecting the facility

Security breaches or vandalism

## 1.3 Life Safety Priority

Life safety shall be the highest priority during any emergency event.

## 1.4 Activation

This Emergency Response Plan shall be activated during any emergency response to a battery-related incident on-site, or when conditions indicate potential for such an incident.

## 1.5 Incident Command System

All personnel shall comply with the orders of the Incident Commander (IC) and command staff. The System Owner/Operator and Subject Matter Experts shall coordinate with the IC to provide technical guidance specific to BESS operations.

# 2. FACILITY OVERVIEW

## 2.1 Site Location and Layout

[INSERT NARRATIVE DESCRIPTION OF FACILITY LOCATION AND NEARBY EXPOSURES]

Site Map: [ATTACH SITE LAYOUT DIAGRAM SHOWING:]

Battery enclosure locations and numbering

Access gates and roads

Emergency disconnect locations

Fire hydrant locations

Evacuation routes and assembly points

Nearby exposures (buildings, residences, schools)

Wind direction (prevailing)

## 2.2 Energy Storage System Specifications

| Battery Chemistry: | [INSERT: LFP, NMC, LTO, etc.] |
| --- | --- |
| Manufacturer/Model: | [INSERT MAKE AND MODEL] |
| Total System Capacity: | [INSERT MW / MWh] |
| Capacity per Unit: | [INSERT kW / kWh per enclosure] |
| Number of Units: | [INSERT NUMBER OF BATTERY ENCLOSURES] |
| DC Voltage Range: | [INSERT VOLTAGE RANGE] |
| Cooling System: | [INSERT: Air-cooled / Liquid-cooled / Immersion] |
| Fire Suppression Type: | [INSERT: Aerosol / Clean agent / Water mist / None] |
| Enclosure Type: | [INSERT: Containerized / Building / Other] |
| Grid Connection Point: | [INSERT UTILITY INTERCONNECTION DETAILS] |
| Remote Monitoring: | [INSERT: Yes/No and monitoring center details] |

# 3. EMERGENCY CONTACT INFORMATION

IN CASE OF EMERGENCY CALL 911

Immediately following 911, contact:

## 3.1 Immediate Response Contacts

| Organization | Primary Contact | Phone Number | Email/Notes |
| --- | --- | --- | --- |
| Local Fire Department | [Fire Chief Name] | [Phone] | [Non-emergency line] |
| Local Police Department | [Contact Name] | [Phone] | [Non-emergency line] |
| System Owner/Operator | [24/7 Contact] | [Phone] | [Email] |
| Network Operations Center | [NOC Contact] | [Phone] | [Monitoring portal URL] |
| Utility Emergency Line | [Utility Name] | [Phone] | [Account/Circuit ID] |

## 3.2 Technical Support Contacts

| Organization | Primary Contact | Phone Number | Email/Notes |
| --- | --- | --- | --- |
| Battery Manufacturer | [Company Name] | [24/7 Emergency Line] | [Model/Serial #s] |
| Inverter/PCS Manufacturer | [Company Name] | [Technical Support] | [Model/Serial #s] |
| Fire Suppression Provider | [Company Name] | [Emergency Service] | [System type/ID] |
| Site Maintenance Contractor | [Company Name] | [On-call Contact] | [Contract details] |

## 3.3 Regulatory and Stakeholder Contacts

| Organization | Primary Contact | Phone Number | Email/Notes |
| --- | --- | --- | --- |
| Fire Marshal | [Name/Office] | [Phone] | [Jurisdiction] |
| Environmental Agency | [Agency Name] | [Phone] | [Permit/ID numbers] |
| Insurance Carrier | [Company Name] | [Claims Line] | [Policy number] |
| Legal/Corporate | [Contact Name] | [Phone] | [Escalation threshold] |

NOTE: This contact list must be reviewed and updated quarterly. Post copies at all site entrances, in the control room, and provide to local fire department.

# 4. BESS-SPECIFIC HAZARDS

Battery Energy Storage Systems present unique hazards that differ from traditional electrical facilities. Understanding these hazards is critical for safe emergency response.

## 4.1 Thermal Runaway

Definition: A chemical process where self-heating in a battery cell exceeds the rate of cooling, causing high internal temperatures, melting, off-gassing/venting, and potentially fire or explosion.

Causes:

Thermal abuse (external heat exposure)

Mechanical abuse (impact, crushing, penetration)

Electrical abuse (overcharging, external short circuit)

Internal short circuit from manufacturing defects

Development of metallic dendrites over time

WARNING: Thermal runaway can propagate from cell to cell, affecting entire modules or racks.

## 4.2 Fire and Re-Ignition Risk

Lithium-ion battery fires have unique characteristics:

Burn extremely hot (1,000-1,500°C / 1,800-2,700°F)

Are not easily extinguished by conventional methods

May burn for hours until all fuel is consumed

Can re-ignite hours or even days after apparent extinguishment

Produce large quantities of toxic smoke and gases

CRITICAL: Do NOT assume a battery fire is completely out. Maintain fire watch and monitoring for minimum 24 hours.

## 4.3 Toxic Gas Release

Battery failures and fires release large quantities of toxic and flammable gases that pose serious inhalation hazards.

Common gases released (varies by chemistry):

Hydrogen fluoride (HF) - Extremely toxic, corrosive

Carbon monoxide (CO) - Colorless, odorless, toxic

Carbon dioxide (CO₂) - Asphyxiant at high concentrations

Hydrogen (H₂) - Flammable, explosive at 4-75% concentration

Methane, ethane, other hydrocarbons - Flammable

Volatile organic compounds (VOCs) - Chemistry dependent

PPE REQUIREMENT: Self-Contained Breathing Apparatus (SCBA) is required for entry during or after any off-gassing or fire event.

## 4.4 Explosion Risk

Flammable gases released during thermal runaway can accumulate within battery enclosures. If concentrations reach explosive limits and an ignition source is present, deflagration (explosion) may occur.

SAFETY PERIMETERS: Minimum 100-150 feet from affected enclosures. Stay at angles to enclosure sides, not in direct alignment with doors or vents.

## 4.5 Electrical Hazards

Shock Hazard:

BESS systems operate at high DC voltages (typically 1,000-1,500 VDC). Batteries retain charge even after apparent shutdown - this is called "stranded energy."

Arc Flash Hazard:

DC arc flash incidents can be more severe than AC equivalents due to the difficulty of extinguishing DC arcs. Arc flash boundaries must be established per system specifications.

VERIFICATION REQUIRED: Always test for zero energy state. NEVER assume a system is de-energized based on visual indicators alone.

## 4.6 Chemical Hazards

Additional chemical hazards at BESS facilities may include:

Battery electrolyte (lithium salts in organic solvents)

Coolant/glycol leaks (liquid-cooled systems)

Refrigerant leaks (HVAC systems)

Fire suppression agent residue

Acidic runoff from firefighting water

[INSERT MANUFACTURER-SPECIFIC CHEMICAL HAZARD INFORMATION AND SDS REFERENCES]

# 5. EMERGENCY RESPONSE PROCEDURES

The following procedures provide guidance for specific emergency scenarios. These procedures are BESS-specific and go beyond traditional electrical facility emergency response.

UNIVERSAL RULE: When in doubt, evacuate and call 911. Coordinate with System Owner/Operator before any system operations.

## 5.1 Fire or Thermal Runaway Incident

IMMEDIATE ACTIONS (First 60 Seconds):

1. EVACUATE ALL PERSONNEL - Sound alarm and initiate facility evacuation

2. CALL 911 - Report "Battery Energy Storage System fire" with specific location

3. CALL SYSTEM OWNER/OPERATOR - Use emergency contact list

4. ESTABLISH SAFETY PERIMETER - Minimum 150 feet (or per manufacturer specs)

5. ACCOUNT FOR PERSONNEL - Confirm all at assembly point

6. DO NOT ATTEMPT SUPPRESSION - Unless trained firefighter with proper equipment

DO NOT:

Attempt to open battery enclosures

Use water unless specifically approved by manufacturer

Attempt emergency stops without System Owner coordination

Re-enter facility for any reason

Assume systems are de-energized

Information for First Responders:

Provide fire department with:

This Emergency Response Plan

Battery chemistry and capacity (from Section 2.2)

Location of electrical isolation points

Site layout showing access routes

Manufacturer emergency contact information

Fire suppression system information

Known wind direction (for smoke/gas dispersion)

Post-Incident Actions:

Maintain fire watch for minimum 24 hours (re-ignition risk)

Continuous gas monitoring until confirmed safe levels

Isolate affected units from electrical system

Thermal imaging to verify cooling

Do not disturb scene until investigation authorized

Coordinate with manufacturer for damage assessment

Initiate post-incident review process (Section 9)

## 5.2 Electrical Shock or Arc Flash Incident

IMMEDIATE ACTIONS:

1. DO NOT TOUCH VICTIM if still in contact with energized equipment

2. CALL 911 - Report electrical emergency and medical need

3. DE-ENERGIZE SOURCE - Use emergency disconnect if safe and qualified to do so

4. CLEAR AREA - Establish minimum 10-foot safety boundary

5. CONTACT SYSTEM OWNER - Report incident and electrical status

6. BEGIN CPR - Only after victim is clear of electrical source and if trained

Arc Flash Considerations:

BESS systems operate at high DC voltages (typical 1000-1500 VDC)

DC arc flash can be more severe than AC equivalents

Arc flash boundaries must be established per system specifications

Only qualified electrical workers with proper PPE may enter boundaries

Full arc-rated PPE required: suit, face shield, gloves, hearing protection

System Isolation Protocol:

WARNING: Improper isolation can worsen conditions or impact grid stability.

Coordinate with System Owner/Operator before any shutdown

Follow manufacturer-specific de-energization procedures

Verify zero energy state (test, do not assume)

Implement lockout/tagout per facility procedures

Maintain lockout until authorized to restore

Document all actions taken

Post-Incident Actions:

Secure area until qualified personnel assess damage

Conduct root cause analysis

Review arc flash study and update if needed

Inspect all affected equipment before energizing

Update training and procedures based on findings

## 5.3 Toxic Gas Release or Off-Gassing Event

IMMEDIATE ACTIONS:

1. EVACUATE IMMEDIATELY - Toxic gas requires immediate egress

2. DON SCBA - If available and trained; otherwise evacuate upwind

3. ACTIVATE VENTILATION - If safe to do so remotely

4. CALL 911 - Report toxic gas release from battery system

5. ESTABLISH UPWIND ASSEMBLY - At designated safe location

6. CONTACT HAZMAT TEAM - If available in jurisdiction

Gas Detection Requirements:

Hydrogen fluoride (HF) - Extremely toxic, specialized detection required

Carbon monoxide (CO) - Colorless, odorless, continuous monitoring

Volatile organic compounds (VOCs) - Chemistry-specific

Lower explosive limit (LEL) - Combustible gas monitoring

Oxygen levels - Ensure adequate before entry

Re-Entry Protocol:

NO RE-ENTRY until ALL of the following conditions are met:

Atmosphere testing confirms safe levels of all target gases

Ventilation system has operated for [INSERT MANUFACTURER TIME REQUIREMENT]

Incident Commander authorizes re-entry

Continuous gas monitoring established for re-entry team

Full PPE including SCBA worn by entry team

Two-person buddy system with continuous communication

## 5.4 Chemical Spill or Coolant Leak

IMMEDIATE ACTIONS:

1. EVACUATE AFFECTED AREA - Move personnel to safe location

2. VENTILATE - Open doors/activate ventilation if safe to do so

3. DON PPE - Chemical-resistant gloves, goggles, respirator as appropriate

4. CONTAIN SPILL - Use absorbent materials, berms, or spill kits

5. CONTACT SYSTEM OWNER - Report spill type and extent

6. CALL 911 - If large spill or if personnel exposed

Spill Response Equipment Required:

[INSERT LOCATION OF SPILL KITS AND CONTENTS]

Post-Incident Actions:

Dispose of contaminated materials per hazardous waste protocols

Decontaminate affected area

Inspect for equipment damage or ongoing leaks

Review SDS for specific chemical involved

Document spill type, volume, and response actions

## 5.5 Natural Disaster (Earthquake, Flood, Severe Weather)

IMMEDIATE ACTIONS:

1. PROTECT PERSONNEL - Seek shelter or evacuate as appropriate

2. SHUT DOWN SYSTEM - If safe to do so and if authorized

3. EVACUATE AFTER IMMEDIATE DANGER - Once safe to move

4. CONTACT SYSTEM OWNER - Report facility status

5. NOTIFY UTILITY - Report potential grid impact

6. CALL 911 - If injuries, damage, or facility compromise

Post-Event Inspection (Before Re-Energizing):

Structural integrity of all enclosures and foundations

Water intrusion or flood damage

Damage to electrical connections and cables

BMS and monitoring system functionality

Fire detection and suppression system status

Ventilation system operation

No signs of thermal events or off-gassing

CRITICAL: Resume operations ONLY after safety clearance from qualified engineer and System Owner/Operator.

## 5.6 Security Breach or Vandalism

IMMEDIATE ACTIONS:

1. DO NOT CONFRONT INTRUDERS - Maintain safe distance

2. CALL 911 - Report security breach and location

3. NOTIFY SECURITY - If contract security service exists

4. CONTACT SYSTEM OWNER - Report breach and potential tampering

5. SECURE AREA - Prevent additional access if safe to do so

6. PRESERVE EVIDENCE - Do not disturb scene

Post-Incident Actions:

Review surveillance footage

Conduct thorough facility inspection for tampering

Check all BMS alarms and system parameters

Test fire detection and suppression systems

Assess for equipment damage or theft

Coordinate with law enforcement investigation

Enhance security measures if warranted

# 6. EVACUATION AND ASSEMBLY POINTS

## 6.1 Evacuation Triggers

Immediate evacuation is required when:

Fire alarm activation

Visible fire, smoke, or flames

BMS alarms indicating thermal runaway

Detection of toxic gas or chemical odors

Explosion or loud noises from battery enclosures

Electrical incident with ongoing hazard

Earthquake or other natural disaster

Ordered by Incident Commander or emergency personnel

## 6.2 Evacuation Routes and Assembly Points

[INSERT FACILITY-SPECIFIC EVACUATION INFORMATION:]

Primary evacuation routes (marked on site map)

Secondary evacuation routes (if primary blocked)

Primary assembly point location: [INSERT LOCATION AND GPS]

Secondary assembly point location: [INSERT LOCATION AND GPS]

Assembly points must be minimum 150 feet from facility

Assembly points must be upwind of prevailing winds

Covered/sheltered assembly areas (if applicable)

## 6.3 Personnel Accountability

Evacuation Procedure:

Exit via nearest safe evacuation route

Do not stop to collect personal items

Assist others if safe to do so

Proceed directly to assembly point

Report to supervisor/accountability officer

Do not re-enter for any reason until authorized

Accountability Process:

Supervisor conducts roll call at assembly point

Report any missing personnel to Incident Commander immediately

Missing persons: provide last known location

Visitor log must be checked if visitors on-site

Do not assume missing persons left voluntarily

## 6.4 Re-Entry Authorization

Re-entry to facility is permitted ONLY when ALL of the following are confirmed:

Emergency resolved and Incident Commander declares safe

Atmosphere testing completed (if applicable) showing safe levels

Structural integrity confirmed (if natural disaster)

No ongoing electrical, fire, or chemical hazards

System Owner/Operator authorizes re-entry

All personnel accounted for

Re-entry briefing conducted explaining current conditions

# 7. EQUIPMENT AND PPE REQUIREMENTS

## 7.1 Personal Protective Equipment by Hazard Type

| Hazard Type | Minimum PPE Required | Additional Requirements |
| --- | --- | --- |
| Fire/Thermal Runaway | Full firefighter PPE SCBA | Only trained firefighters Stay at safe distance |
| Toxic Gas Release | SCBA Chemical-resistant suit | Gas detection equipment Two-person entry |
| Electrical Work | Arc-rated PPE Voltage-rated gloves Face shield | Per arc flash study Insulated tools only |
| Chemical Spill | Chemical-resistant gloves Goggles Respirator | Per SDS for specific chemical Spill containment kit |
| Routine Operations | Safety glasses Closed-toe shoes Long pants | Hard hat in designated areas |

## 7.2 Emergency Response Equipment

[INSERT FACILITY-SPECIFIC EQUIPMENT LOCATIONS AND QUANTITIES:]

Fire extinguishers: [CLASS AND LOCATIONS]

First aid kits: [LOCATIONS]

Spill containment kits: [LOCATIONS]

Emergency shutdown switches: [LOCATIONS]

Gas detection equipment: [TYPE AND LOCATIONS]

Communication devices: [TYPE - radios, phones, etc.]

Emergency lighting: [LOCATIONS]

AED (Automated External Defibrillator): [LOCATION if available]

Fire suppression equipment: [TYPE AND OPERATION]

## 7.3 Equipment Inspection and Maintenance

All emergency equipment must be inspected and maintained per the following schedule:

| Equipment | Inspection Frequency | Responsible Party |
| --- | --- | --- |
| Fire extinguishers | Monthly visual/Annual service | [INSERT] |
| First aid kits | Monthly | [INSERT] |
| Gas detection equipment | Monthly calibration | [INSERT] |
| Fire suppression system | Per manufacturer specs | [INSERT] |
| Emergency lighting | Monthly test | [INSERT] |
| PPE | Before each use/Annual | [INSERT] |

# 8. TRAINING AND DRILLS

## 8.1 Required Training

All personnel must receive BESS-specific emergency response training appropriate to their role. Training must be completed before personnel are authorized for independent site access.

| Personnel Category | Required Training | Frequency |
| --- | --- | --- |
| All Site Personnel | BESS hazards overview Evacuation procedures Emergency contacts | Initial + Annual |
| Operations Staff | All of above plus: Emergency shutdown procedures Fire suppression activation Gas detection systems | Initial + Annual |
| Maintenance Personnel | All of above plus: Electrical safety (NFPA 70E) Lockout/tagout Arc flash PPE | Initial + Annual |
| Emergency Response Team | All of above plus: Incident Command System First responder coordination Post-incident procedures | Initial + Semi-annual |
| Contractors/Visitors | Site safety briefing Evacuation procedures Hazards overview | Before site access |

## 8.2 Emergency Drill Program

Drills shall be conducted on the following schedule:

Evacuation drill: Quarterly (minimum)

Fire scenario tabletop exercise: Semi-annually

Full-scale emergency simulation: Annually

First responder coordination exercise: Annually (with local fire department)

Drill Objectives:

Test emergency notification systems

Practice evacuation routes and assembly procedures

Verify personnel accountability process

Identify gaps in procedures or training

Practice coordination with System Owner/Operator

Build muscle memory for emergency actions

Test emergency equipment functionality

## 8.3 Drill Documentation

After each drill, the following documentation must be completed:

Drill date, time, and type

Participating personnel

Scenario description

Observations and timeline

Identified issues or gaps

Corrective actions required

Action item assignments and due dates

Drill reports shall be maintained for minimum [INSERT RETENTION PERIOD] years.

## 8.4 Training Records

Training records must be maintained including:

Employee name and position

Training topic and date completed

Instructor/training provider

Test scores or competency verification (if applicable)

Certification expiration dates

Refresher training due dates

# 9. POST-INCIDENT REVIEW PROCESS

## 9.1 Review Timeline

A post-incident review must be conducted within 48 hours for any of the following:

Any fire or thermal runaway event

Evacuation activation (emergency or drill)

Toxic gas release or off-gassing

Electrical incident resulting in injury or equipment damage

Natural disaster affecting facility

Security breach or vandalism

Near-miss incidents with potential for serious consequence

## 9.2 Review Team

Post-incident review team should include:

System Owner/Operator representative

Facility safety director or manager

Personnel directly involved in incident response

Equipment manufacturer representative (for equipment failures)

Fire department representative (for fire/evacuation events)

Legal/insurance representative (for significant incidents)

## 9.3 Review Process

The review process includes:

1. Incident timeline reconstruction

2. Root cause analysis

3. Response effectiveness evaluation

4. Equipment performance assessment

5. Communication effectiveness review

6. Training adequacy assessment

7. Identification of corrective actions

## 9.4 Documentation Requirements

Post-incident report must include:

Incident date, time, and location

Incident description and timeline

Personnel involved and actions taken

Equipment performance

BMS data and alarms (if applicable)

Photos/video documentation

Root cause analysis findings

Corrective actions with assignments and due dates

ERP updates required

Lessons learned

Report Distribution:

Post-incident reports shall be distributed to:

System Owner/Operator

Facility management

All personnel involved in response

Equipment manufacturers (for equipment-related incidents)

Insurance carrier (as required)

Regulatory agencies (as required)

Local fire department (for coordination improvement)

## 9.5 Corrective Action Tracking

All corrective actions identified in the post-incident review must be tracked to completion.

| Action Item | Assigned To | Due Date | Status | Completion Date |
| --- | --- | --- | --- | --- |
| [Example: Update ERP Section 5.1] | [Safety Manager] | [Date] | [Open/Closed] | [Date completed] |

[INSERT TABLE WITH FACILITY-SPECIFIC CORRECTIVE ACTION TRACKING]

# 10. DOCUMENT CONTROL AND UPDATES

## 10.1 Document Ownership

| Document Owner: | [INSERT NAME/TITLE] |
| --- | --- |
| Approval Authority: | [INSERT NAME/TITLE] |
| Technical Review: | [INSERT NAME/TITLE - System Owner/Operator] |
| Annual Review Due: | [INSERT DATE] |

## 10.2 Review and Update Schedule

This ERP must be reviewed and updated on the following schedule:

Annual review (minimum) - even if no changes

After any significant incident

When facility modifications affect emergency response

When equipment is added, removed, or upgraded

When manufacturer updates emergency procedures

When regulatory requirements change

After emergency drills identify gaps

When key personnel or contact information changes

## 10.3 Distribution List

Current copies of this ERP must be maintained at the following locations:

Facility control room or operations center

All facility entrance gates

System Owner/Operator offices

Local fire department (provide to Fire Marshal)

Maintenance contractor offices

Digital copy accessible to all authorized personnel

[INSERT ADDITIONAL LOCATIONS]

## 10.4 Version Control

Document revision history:

| Version | Date | Description of Changes | Author |
| --- | --- | --- | --- |
| 1.0 | [INSERT DATE] | Initial release | [INSERT NAME] |
| [X.X] | [INSERT DATE] | [Description] | [INSERT NAME] |
| [X.X] | [INSERT DATE] | [Description] | [INSERT NAME] |

# APPENDICES

## Appendix A: Site Layout and Evacuation Map

[ATTACH SITE MAP SHOWING:]

Battery enclosure locations with unit numbers

Access roads and gates

Evacuation routes (primary and secondary)

Assembly points (primary and secondary)

Fire hydrant locations

Emergency disconnect locations

First aid kit and emergency equipment locations

Prevailing wind direction

North arrow and scale

## Appendix B: Emergency Contact Quick Reference Card

[ATTACH WALLET-SIZED EMERGENCY CONTACT CARD FOR ALL PERSONNEL]

Card should include:

911

System Owner/Operator 24/7 number

Local fire department

Facility manager/supervisor

Network Operations Center

Emergency assembly point location

## Appendix C: First Responder Information Sheet

[ATTACH ONE-PAGE SUMMARY FOR FIRE DEPARTMENT INCLUDING:]

Battery chemistry and hazard overview

Total system capacity (MW/MWh)

Electrical voltage levels

Fire suppression system type and activation

Recommended approach and safety distances

Emergency contact for System Owner/Operator

Site layout with access routes

Special hazards (toxic gases, explosion risk, re-ignition)

PPE requirements (SCBA mandatory)

## Appendix D: Incident Report Form

[ATTACH BLANK INCIDENT REPORT TEMPLATE]

Form should capture:

Date, time, location of incident

Type of incident

Personnel involved and witnesses

Sequence of events

Actions taken

Equipment involved

Injuries or damage

Emergency services response

Photos/diagrams

Immediate corrective actions

## Appendix E: Manufacturer Emergency Procedures

[ATTACH MANUFACTURER-SPECIFIC EMERGENCY RESPONSE PROCEDURES]

Include:

Battery system emergency shutdown procedures

Fire suppression system operation manual

BMS alarm guide and response

Manufacturer 24/7 emergency contact

Specific hazards by battery chemistry

Approved fire suppression methods

Post-incident inspection requirements

## Appendix F: Safety Data Sheets (SDS)

[ATTACH SDS FOR ALL CHEMICALS ON-SITE]

Include SDS for:

Battery electrolyte

Coolant/glycol (if liquid-cooled)

Fire suppression agent

Refrigerants

Cleaning chemicals

Maintenance materials

## Appendix G: Regulatory Requirements

[ATTACH OR REFERENCE APPLICABLE REGULATIONS]

May include:

NFPA 855: Standard for Energy Storage Systems

NFPA 70E: Electrical Safety in the Workplace

OSHA 1910 Subpart S: Electrical

Local fire code requirements

Utility interconnection requirements

Environmental regulations

State/local emergency planning requirements

# DOCUMENT APPROVAL

This Emergency Response Plan has been reviewed and approved by:

| Facility Manager: | Signature: ___________________ | Date: __________ |
| --- | --- | --- |
| System Owner/Operator: | Signature: ___________________ | Date: __________ |
| Safety Director: | Signature: ___________________ | Date: __________ |
| Fire Marshal (Acknowledgment): | Signature: ___________________ | Date: __________ |
| Date of Approval: | Signature: ___________________ | [INSERT DATE] |

Next Review Due: [INSERT DATE - One year from approval]